## Free Calculation
max rain rate ( l/ s ha ): |  |  | 150 | D please add here your rain rate!
Maximum length of channel run
Catchment | Inflow volume | MAXI 100 | Overflow | MAXI 150 | Overflow | MAXI 200 | Overflow | MAXI 300 | Overflow
depth | l/ s m | Height 210 mm | volume l / s | Height 260 mm | volume l / s | Height 310 mm | volume l / s | Height 400 mm | volume l / s
5 m | 0.0675 | 50 | 3.375 | 50 | oversized | 50 | oversized | 50 | oversized
10 m | 0.135 | 40.7407 | 5.5 | 50 | oversized | 50 | oversized | 50 | oversized
15 m | 0.2025 | 27.1605 | 5.5 | 50 | oversized | 50 | oversized | 50 | oversized
20 m | 0.27 | 20.3704 | 5.5 | 46.2963 | 12,50 | 50 | oversized | 50 | oversized
25 m | 0.3375 | 16.2963 | 5.5 | 37.037 | 12,50 | 50 | oversized | 50 | oversized
30 m | 0.405 | 13.5802 | 5.5 | 30.8642 | 12,50 | 50 | oversized | 50 | oversized
35 m | 0.4725 | 11.6402 | 5.5 | 26.455 | 12,50 | 46.5608 | 22,00 | 50 | oversized
40 m | 0.54 | 10.1852 | 5.5 | 23.1481 | 12,50 | 40.7407 | 22,00 | 50 | oversized
45 m | 0.6075 | 9.0535 | 5.5 | 20.5761 | 12,50 | 36.214 | 22,00 | 50 | oversized
50 m | 0.675 | 8.1481 | 5.5 | 18.5185 | 12,50 | 32.5926 | 22,00 | 50 | oversized
60 m | 0.81 | 6.7901 | 5.5 | 15.4321 | 12,50 | 27.1605 | 22,00 | 50 | oversized
70 m | 0.945 | 5.8201 | 5.5 | 13.2275 | 12,50 | 23.2804 | 22,00 | 46.0317 | 43,50
Length of 50 and more meters are unsuitable. This drainage channels are oversized
Example of the calculation:
correction value 0,9 (90 % of the rain rate is the actual inflow)
qr = r/ 10000 • 0,9 • E
Qr = qr • L
Outflow volume Qr (l / s)
Inflow volume qr (l / s m)
Section length L (m)
Rain rate r (l/ s ha) |  |  | catchments depth E |  |  |  | catchments depth E
Catchments depth E (m) | [8 empty] | The ideal length between two outlet pipes is 30 m
|  |  | length of a channel run |  |  | length of a channel run
Channel without slope
The ideal length between two outlet pipes is 30 m

## MAXI 100
max regnmængde ( l/ s ha ): |  |  | 230 | D Indsæt din regnintensitet her
Maximum length of MAXI/ TOP channel run
Opstuvnings | Inflow volume | MAXI 100 | Overflow | MAXI 100 | Overflow | MAXI 100 | Overflow | MAXI 100 | Overflow | MAXI 100 | Overflow
bredde | l/ s m | Height 160 mm | volume l / s | Height 185 mm | volume l / s | Height 210 mm | volume l / s | Height 235 mm | volume l / s | Height 260 mm | volume l / s
5 m | 0.1035 | 25.1207 | 2.6 | 39.1304 | 4.05 | 50 | oversized | 50 | oversized | 50 | oversized
10 m | 0.207 | 12.5604 | 2.6 | 19.5652 | 4.05 | 26.57 | 5,50 | 34.541 | 7,15 | 42.512 | 8,80
15 m | 0.3105 | 8.3736 | 2.6 | 13.0435 | 4.05 | 17.7133 | 5,50 | 23.0274 | 7,15 | 28.3414 | 8,80
20 m | 0.414 | 6.2802 | 2.6 | 9.7826 | 4.05 | 13.285 | 5,50 | 17.2705 | 7,15 | 21.256 | 8,80
25 m | 0.5175 | 5.0242 | 2.6 | 7.8261 | 4.05 | 10.628 | 5,50 | 13.8164 | 7,15 | 17.0048 | 8,80
30 m | 0.621 | 4.1868 | 2.6 | 6.5217 | 4.05 | 8.8567 | 5,50 | 11.5137 | 7,15 | 14.1707 | 8,80
35 m | 0.7245 | 3.5887 | 2.6 | 5.5901 | 4.05 | 7.5914 | 5,50 | 9.8689 | 7,15 | 12.1463 | 8,80
40 m | 0.828 | 3.1401 | 2.6 | 4.8913 | 4.05 | 6.6425 | 5,50 | 8.6353 | 7,15 | 10.628 | 8,80
45 m | 0.9315 | 2.7912 | 2.6 | 4.3478 | 4.05 | 5.9044 | 5,50 | 7.6758 | 7,15 | 9.4471 | 8,80
50 m | 1.035 | 2.5121 | 2.6 | 3.913 | 4.05 | 5.314 | 5,50 | 6.9082 | 7,15 | 8.5024 | 8,80
55 m | 1.1385 | 2.2837 | 2.6 | 3.5573 | 4.05 | 4.8309 | 5,50 | 6.2802 | 7,15 | 7.7295 | 8,80
60 m | 1.242 | 2.0934 | 2.6 | 3.2609 | 4.05 | 4.4283 | 5,50 | 5.7568 | 7,15 | 7.0853 | 8,80
65 m | 1.3455 | 1.9324 | 2.6 | 3.01 | 4.05 | 4.0877 | 5,50 | 5.314 | 7,15 | 6.5403 | 8,80
Længde på 50m eller længere er ikke hensigtsmæssig. Renden er overdimensioneret
Example of the calculation: | [8 empty] | Ideal længden mellem to udløb er 30m
correction value 0,9 (90 % of the rain rate is the actual inflow)
qr = r/ 10000 • 0,9 • E | [6 empty] | Opstuvnings bredde
Qr = qr • L
Outflow volume Qr (l / s)
Inflow volume qr (l / s m)
Section length L (m)
Rain rate r (l/ s ha)
Catchments depth E (m)
Længde af stregen
Length of 50 and more meters are unsuitable. This drainage channels are oversized
The ideal length between two outlet pipes is 30 m
Opstuvningsareal

## MAXI 150-300
max rain rate ( l/ s ha ): |  |  | 190 | D please add here your rain rate!
Maximum length of MAXI channel run
Catchment | Inflow volume | MAXI 150 | Overflow | MAXI 150 | Overflow | MAXI 150 | Overflow | MAXI 200 | Overflow | MAXI 300 | Overflow
depth | l/ s m | Height 210 mm | volume l / s | Height 260 mm | volume l / s | Height 310 mm | volume l / s | Height 310 mm | volume l / s | Height 400 mm | volume l / s
10 m | 0.171 | 50 | oversized | 50 | oversized | 50 | oversized | 50 | oversized | 50 | oversized
15 m | 0.2565 | 39.3762 | 10,10 | 48.7329 | 12,50 | 50 | oversized | 50 | oversized | 50 | oversized
20 m | 0.342 | 29.5321 | 10,10 | 36.5497 | 12,50 | 49.7076 | 17,00 | 50 | oversized | 50 | oversized
25 m | 0.4275 | 23.6257 | 10,10 | 29.2398 | 12,50 | 39.7661 | 17,00 | 50 | oversized | 50 | oversized
30 m | 0.513 | 19.6881 | 10,10 | 24.3664 | 12,50 | 33.1384 | 17,00 | 42.8849 | 22,00 | 50 | oversized
35 m | 0.5985 | 16.8755 | 10,10 | 20.8855 | 12,50 | 28.4043 | 17,00 | 36.7585 | 22,00 | 50 | oversized
40 m | 0.684 | 14.7661 | 10,10 | 18.2748 | 12,50 | 24.8538 | 17,00 | 32.1637 | 22,00 | 50 | oversized
45 m | 0.7695 | 13.1254 | 10,10 | 16.2443 | 12,50 | 22.0922 | 17,00 | 28.59 | 22,00 | 50 | oversized
50 m | 0.855 | 11.8129 | 10,10 | 14.6199 | 12,50 | 19.883 | 17,00 | 25.731 | 22,00 | 50 | oversized
55 m | 0.9405 | 10.739 | 10,10 | 13.2908 | 12,50 | 18.0755 | 17,00 | 23.3918 | 22,00 | 46.2519 | 43,50
60 m | 1.026 | 9.844 | 10,10 | 12.1832 | 12,50 | 16.5692 | 17,00 | 21.4425 | 22,00 | 42.3976 | 43,50
65 m | 1.1115 | 9.0868 | 10,10 | 11.2461 | 12,50 | 15.2946 | 17,00 | 19.7931 | 22,00 | 39.1363 | 43,50
75 m | 1.2825 | 7.8752 | 10,10 | 9.7466 | 12,50 | 13.2553 | 17,00 | 17.154 | 22,00 | 33.9181 | 43,50
Length of 50 and more meters are unsuitable. This drainage channels are oversized
Example of the calculation: | [7 empty] | The ideal length between two outlet pipes is 30 m
correction value 0,9 (90 % of the rain rate is the actual inflow)
qr = r/ 10000 • 0,9 • E | [7 empty] | Catchments depth
Qr = qr • L
Outflow volume Qr (l / s)
Inflow volume qr (l / s m)
Section length L (m)
Rain rate r (l/ s ha)
Catchments depth E (m)
Length of a channel run
Catchments area